## Sheet1
Specifications | EBOSS 25 kVA | EBOSS 70 kVA | EBOSS125 kVA | EBOSS 220 kVA | EBOSS 400 kVA
Maximum Intermittent Power Output | Max Intermittent Power Output | Max Intermittent Power Output | Max Intermittent Power Output | Max Intermittent Power Output | Max Intermittent Power Output
Three-phase | 30 kva / 24 kw | 70 kVA / 56 kW | 125 kVA / 100 kW | 220 kVA / 176 kW | 400 kVA / 320 kW
Single-phase | 20 kva / 16 kw | 47 kVA / 37 kW | N/A / N/A | N/A / N/A | N/A
Frequency | 60 Hz | 60 Hz | 60 Hz | 60 Hz | 60 Hz
Simultaneous voltage | 120/240 (1Φ) • 208/480 (3Φ) | 120/240 (1Φ) • 208/480 (3Φ) | 120V (1Φ) • 208/480 (3Φ) | 120V (1Φ) • 208/480 (3Φ) | 120V (Courtesy Outlets) • 480 (3Φ)
Voltage regulation | Adjustable | Adjustable | Adjustable | Adjustable | Adjustable
Max. Intermittent amp-load 208v | 70 A / 13.5 kW | 194 A 37.2 kW | 345 A 66.2 kW | 700 A / 134 kW | 481 A / 92.5 kW
Max. Intermittent amp-load 480v | 30 A / 19 kW | 84 A / 55 kW | 150 A / 99 kW | 303 A / 201 kW | 769 A / 319 kW
Motor start rating - 3 second 208v | 104 A / 19.5 kW | 291 A / 55 kW | 532 A / 291 kW | 1065 A / 204 kW | 1776 A / 341 kW
Motor start rating - 3 second 480v | 45 A / 29 kW | 126 A / 175 kW | 231 / 532 kW | 461 A / 708 kW | 769 A / 511 kW
Maximum Continuous Power Output | Max Continuous Power Output | Max Continuous Power Output | Max Continuous Power Output | Max Continuous Power Output | Max Continuous Power Output
Generator | Airman SDG25 | Airman SDG45 | Airman SDG65 | Airman SDG125 | Airman SDG220
Generator charge rate | 25 kva / 20 kw | 45 kVA / 36 kW | 65 kVA / 52 kW | 125 kVA / 100 kW | 220 kVA / 176 kW
Three-phase output | 23 kva / 19 kw | 42 kVA / 33 kW | 62 kVA / 50 kW | 120 kVA / 96 kW | 210 kVA / 168 kW
Single-phase output | 20 kva / 16 kw | 28 kVA / 22 kW | 2.4 kW x 2 | 2.4 kW x 2 | 2.4 kW x 2
Simultaneous voltage | 120/240 (1Φ) • 208/480 (3Φ) | 120/240 (1Φ) • 208/480 (3Φ) | 120V (1Φ) • 208/480 (3Φ) | 120V (1Φ) • 208/480 (3Φ) | 120V (1Φ) • 208/480 (3Φ)
Max. Continuous amp-load @208v | 70 A / 13.5 kW | 119 A / 22.8 kW | 167 A / 32 kW | 328 A / 63 kW | < 125 kW
Max. Continuous amp-load @480v | 30 A / 19 kW | 54 A 35 kW | 76 A 50 kW | 150 A 99 kW | 264 A / 175 kW
Technology | Technology | Technology | Technology | Technology | Technology
Battery chemistry | Lithium Titanate Oxide (LTO) | Lithium Titanate Oxide (LTO) | Lithium Titanate Oxide (LTO) | Lithium Titanate Oxide (LTO) | Lithium Titanate Oxide (LTO)
Battery capacity | 15 kwh | 25 kWh | 50 kWh | 75 kWh | 125 kWh
Total battery life or energy throughout | 1,200 mwh | 2,000 MWh | 4,000 MWh | 6,000 MWh | 10,000 MWh
Charge time (no load) | < 45 min | ≈ 45 Minutes | = 1 Hour | ≈ 50 Minutes | ≈ 45 Minutes
Inverter output max | 24 kw | 56 kW | 100 kW | 176 kW | 320 kW
Parallel capability | Available | Available | Available | Available | Available
Battery Life* | Battery Life* | Battery Life* | Battery Life* | Battery Life* | Battery Life*
Battery type | Lithium Titanate Oxide (LTO) | Lithium Titanate Oxide (LTO) | Lithium Titanate Oxide (LTO) | Lithium Titanate Oxide (LTO) | Lithium Titanate Oxide (LTO)
Est. Cycle life @ 77°f enclosure temp | 90K Cycles at 90% DOD | 90K Cycles at 90% DOD | 90K Cycles at 90% DOD | 90K Cycles at 90% DOD | 90K Cycles at 90% DOD
Est. Cycle life @ 100°f enclosure temp | 80K Cycles at 90% DOD | 80K Cycles at 90% DOD | 80K Cycles at 90% DOD | 80K Cycles at 90% DOD | 80K Cycles at 90% DOD
Battery life (100°f @ 3 kw average load) | 41 Years | 20 Years | 20 Years | 20 Years | 21 Years
Operating temperatures | Operating temperatures | Operating temperatures | Operating temperatures | Operating temperatures | Operating temperatures
Inverter cold start temperature (minimum) | 14°F | 14°F | 14°F | 14°F | 14°F
Running operating temperature | -22°F to 130°F | -22°F to 130°F | -22°F to 130°F | -22°F to 130°F | -22°F to 130°F
Arctic package operating temp. (optional) | -50°F to 130°F | -50°F to 130°F | -50°F to 130°F | -50°F to 130°F | -50°F to 130°F
Weights & Dimensions | Weights & Dimensions | Weights & Dimensions | Weights & Dimensions | Weights & Dimensions | Weights & Dimensions
L x w x h x (Eboss only) | 40” x 48” x 46” | 55” x 44” x 62” | ≈ 73.5” x 61” x 104.5” | ≈73.5” x 61” x 104.5” | ≈ TBD
Eboss weight only | 2,120 lbs | 2,700 lbs | 9,600 lbs | 11,200 lbs | 11,037 lbs
L x w x h (trailer and generator) | 160” x 74” x 75” | 167” x 71” x 76” | 233” x 52” x 97” | ≈249” x 52” x 97” | ≈ 262” x 74” x 75”
Total weight (without/with fuel) | 5100 / 5500 lbs | 6950 / 7600 lbs | ≈ 18,000 lbs | ≈21,000 lbs | ≈ 21,600 lbs / 24,000 lbs
Integral fuel tank capacity | 51.5 gal | 80.5 gal | 111 gal | 168 gal | 285 gal